I have a model to quantify future LV grid loading. It is based on todays grid capacities (mainly transformers and cables) and a household load estimation. With a power flow I get values of overloading. e.g., an overloading of a transformer that requires its substitution or an overloaded cable that requires an additional parallel cable as reinforcement. For now, I dont assume completely new grid supply areas, but just the reinforcement of existing settlement structures.

Vertiefte Recherche

Your current assumption that LV reinforcement can be done without reopening streets is only partially valid: it matches how subsequent parallel cables are often installed in Germany, but it is too optimistic for the first reinforcement of an existing route and for many legacy LV grids without spare ducts.[1][2]
A heuristic cost model for German LV grid expansion can be robustly grounded in official studies; when calibrated to their unit cost ranges, your transformer and cable cost assumptions are broadly defensible, provided you explicitly distinguish first‑time trenching from later cable additions and account for urban–rural differences.[3][2][4]

Street reopening: when the assumption holds and when it does not

German LV grid expansion studies and planning guidelines consistently treat civil engineering (Tiefbau) and street reopening as a dominant cost component for initial cable reinforcement, but not for subsequent parallel cables laid in prepared ducts.[2][3]

- WEI202 / FfE GridSim expansion model
In the LV grid expansion module, parallel cables are added recursively until overloads disappear; cost calculation explicitly distinguishes between “initial installation of a parallel line” (including excavation) and “further parallel lines.”[1]
The model assumes that when the first reinforcement is built, additional empty pipes (Leerrohre) are laid alongside the cable so that later cable additions incur mainly material costs, not renewed Tiefbau.[1]

- Urban planning guidelines (Wintzek 2021)
For urban LV grids, Wintzek explicitly notes that “inner‑städtische Netzbereiche” cannot have streets “in kurzer Zeit beliebig großflächig aufgebrochen,” and that this limitation is one reason to use dynamic load management to delay conventional reinforcement.[2]
This confirms that reopening streets is unavoidable for many initial reinforcements, is a scheduling bottleneck, and cannot be ignored in realistic cost or timing assessments.[2]

- Baden‑Württemberg Verteilnetzstudie (2017)
The cost tables for NS cables and stations include large components for “Erdarbeiten” and “Grund und Boden,” highlighting that civil works are a major driver of cable reinforcement cost, particularly in urban areas.[3]

Implication for your model

- For existing LV feeders built decades ago without spare ducts, assuming “no street reopening” for the first reinforcement is not realistic – you will understate both cost and implementation constraints.[3][2]

- For later reinforcements of routes that already had empty pipes installed in a previous expansion, your assumption is much closer to practice: those can often be modeled as “material + pulling cost” without major Tiefbau.[1][2]

A pragmatic refinement is therefore:

- Model first reinforcement per route with full trenching / street reopening costs.

- Model subsequent parallel cables on that route using an “empty‑pipe” cost level (significantly lower per meter).

This matches the cost logic in WEI202 and Wintzek’s annex and keeps your heuristic realistic without tracking street‑by‑street details.[2][1]

Installation practices and empty‑pipe strategies in German LV grids

The main technical references in your package describe LV expansion in a way that aligns well with the physical logic behind your heuristic model.

- GridSim / WEI202 dissertation (2024)
LV reinforcement is modeled as:

  - Check transformer overload; if necessary, replace with next standard size (250–1000 kVA), and if still overloaded, add a new station.[1]

  - Reinforce overloaded LV lines with parallel cables, using voltage‑band compliance as an absolute criterion.[1]

  - Distinguish cost between first and subsequent parallel lines based on the assumption that “zusätzliche Leerrohre” are laid at first reinforcement, so only the first parallel cable bears the high excavation cost.[1]

- Urban LV guideline “PuBStadt” (Wintzek 2021)
Wintzek recommends, for strategic planning, to:

  - Introduce a second standard NS cable cross‑section (e.g. 240 mm² Al) so that, where a parallel line is undesirable, the existing cable can be replaced once with a larger cross‑section in the same trench.[2]

  - Lay empty pipes in parallel when trenches are opened, to accommodate later cable additions at lower cost.[2]

- Verteilnetzstudie Baden‑Württemberg
Standard expansion variants include: new LV cable sections, transformer replacement, installation of regelbare Ortsnetztransformatoren (rONT), and in MS grid, use of MS‑Spannungsregler.[3]
The study’s methodology is consistent with your approach: use existing settlement structures and grid routes, reinforce via cables and transformers, and only in extreme scenarios consider entirely new grid areas.[3]

Taken together, these sources support the structure of your model (reinforcement within existing settlements through extra cables and transformers) but clearly show that some reopening of streets is structurally unavoidable unless you explicitly model the “first reinforcement” as already completed.[3][2][1]

Benchmark unit costs for LV grid reinforcement

Below is a consolidation of unit cost benchmarks from the Baden‑Württemberg Verteilnetzstudie, Wintzek’s PuBStadt guideline, and related annexes.[3][2]
Values are indicative ranges; you can use them to validate or adjust your heuristic numbers.

LV components (NS level)

Table 1 – NS‑level reinforcement cost benchmarks (per asset)

| Asset / measure | Settlement type | Benchmark cost (order of magnitude) | Source |
| --- | --- | --- | --- |
| NS cable, first installation / replacement | Rural | ~80 000 €/km (incl. earthworks)[3] | BW‑study Tab. 7.1[3] |
|  | Semi‑urban | ~100 000 €/km[3] | BW‑study Tab. 7.1[3] |
|  | Urban | ~125 000 €/km[3] | BW‑study Tab. 7.1[3] |
| NS cable NAYY 4×150 mm², first line | Generic | ~150 000 €/km (incl. Tiefbau)[2] | PuBStadt Tab. 17.2[2] |
| NS cable NAYY 4×150 mm², parallel line | Generic | ~20 000 €/km (mainly material)[2] | PuBStadt Tab. 17.2[2] |
| NS cable NAYY 4×240 mm², first line | Generic | ~200 000 €/km[2] | PuBStadt Tab. 17.2[2] |
| NS cable NAYY 4×240 mm², parallel line | Generic | ~60 000 €/km[2] | PuBStadt Tab. 17.2[2] |
| New LV secondary substation (ONS building) | Any | ~45 000–60 000 € per station[3][2] | BW‑study 10; PuBStadt 17.2[3][2] |
| Replacement LV transformer (ONT, same size) | Any | ~10 000–15 000 € per unit[3][2] | BW‑study 11; PuBStadt 17.2[3][2] |
| New rONT (regelbarer ONT) | Any | ~45 000 € per unit (above regular ONT)[3] | BW‑study 12[3] |
| LV cable operating & maintenance (Opex) | Any | ~2.5 % of CapEx per year (typical assumption)[2] | PuBStadt 17.2[2] |

These figures show that:

- Civil engineering roughly doubles or triples the cost compared with cable+installation alone (compare first vs parallel NS cable lines).[2]

- Urban NS cable reinforcement costs on the order of 125–200 k€/km are entirely plausible, depending on depth, street type, and whether bundled civil costs are fully included.[3][2]

If your heuristic NS cable cost per km including Tiefbau lies within roughly 80–200 k€/km depending on settlement type, it is well supported by these official studies.[2][3]

MS components (medium voltage level, relevant for transformer reinforcement)

Table 2 – MS‑level reinforcement cost benchmarks

| Asset / measure | Settlement type | Benchmark cost | Source |
| --- | --- | --- | --- |
| MS cable NA2XS2Y 3×150‑300 mm², first | Rural | ~130 000 €/km[3] | BW‑study 9[3] |
|  | Semi‑urban | ~145 000 €/km[3] | BW‑study 9[3] |
|  | Urban | ~160 000 €/km[3] | BW‑study 9[3] |
| New MS/LV substation (transformer + UW) | Any | 1.3–3.2 M€ depending on size[3] | BW‑study 6,7[3] |
| MS‑Spannungsregler | Any | ~300 000 € per regulator[3] | BW‑study 6.5[3] |

Your heuristic MS reinforcement costs should, for Germany, be in roughly the 130–160 k€/km range for cable and 1–3 M€ for substation upgrades, scaled to transformer rating.[3]

Macro‑level cost benchmarks (for sanity checking your totals)

To check whether your model’s aggregate cost outputs are reasonable, you can compare them with national and regional projections.

- Bundesnetzagentur “Zustand und Ausbau der Verteilernetze 2022”
For 2022–2032, the BNetzA reports an expected Verteilnetz‑ausbaubedarf of 42.27 bn € across all voltage levels.[4][5]
Of this, 16.42 bn € stems from identified individual measures, while 25.84 bn € comes from aggregated 10‑year planning of lower network levels (MS/NS), derived from DSOs’ experience‑based heuristics rather than detailed project lists.[5][4]
This explicitly confirms that heuristic cost models similar to yours are standard and accepted at regulatory level, especially for LV grids where detailed planning is too short‑term and granular.[4]

- Verteilnetzstudie Baden‑Württemberg (2017)
For Baden‑Württemberg alone, the study finds cumulative MS+NS reinforcement investments in the low single‑digit billion‑euro range by 2030, depending on scenario and use of flexibility, with NS investment roughly one quarter to one third of total.[3]
Scenario variants (e.g. Spitzenkappung, rONT, Sektorenkopplung) change the NS investment by up to ±40 %, showing realistic sensitivity bands your model should also capture.[3]

- WEI202 / DGLA 2045 analysis
Extrapolating characteristic LV grids to Germany, WEI202 finds that ambitious electrification with limited flexibility leads to LV reinforcement needs (transformers + cables) that are roughly twice those in conservative scenarios, with strong regional variation but no absurd outliers compared to dena/BNetzA values.[1]

If your national LV cost results are broadly compatible with:

- tens of billions of euros nationwide over two decades, and

- NS accounting for, say, 20–40 % of total distribution grid reinforcement cost,

then your macro‑level heuristic cost results are in line with these official benchmarks.[4][1][3]

What to adjust or confirm in your heuristic model

1. Distinguish first vs subsequent cable reinforcements

Given the strong cost contrast in the sources, your LV cost model should:

- Use two cost categories for cables per route:

  - First reinforcement (with Tiefbau): ~80–200 k€/km depending on settlement type and cross‑section.[2][3]

  - Further parallel cables (using empty pipes): ~20–60 k€/km.[2]

- Couple the transition between these categories to a state variable: “empty ducts available yes/no.”

This makes your “no street reopening” assumption valid for the second category while keeping the first realistic.[1][2]

2. Transformer cost and sizing

The ranges in BW‑study and PuBStadt support the following heuristics for LV transformers:

- Standard ONT sizes: 630 kVA as the historical standard, with 800 kVA and 1000 kVA increasingly used in progressive electrification scenarios.[2]

- Costs:

  - Replacement (same civil footprint): ~10–15 k€/unit.[3][2]

  - New station including building and switchgear: ~60 k€ for NS ONS, up to 1.3–3.2 M€ at MS level depending on transformer rating.[2][3]

If your transformer cost assumptions fall into these bands and you model the stepwise up‑sizing (e.g. 630→800→1000 kVA) plus occasional new station construction for heavily loaded grids, they are well grounded.[1][3][2]

3. Urban vs rural differentiation

All major studies show significant cost and loading differences between rural, suburban, and urban LV grids.[1][3]

- Rural grids: longer feeders, higher share of feed‑in issues (PV), and more expensive per‑grid reinforcement due to long cable lengths, but cable €/km can be somewhat lower than dense urban streets.[1][3]

- Urban grids: shorter feeders, load‑driven expansion (EV, heat pumps), and higher unit costs due to complex Tiefbau, traffic management, and coordination with other utilities.[3][2]

At minimum, your heuristics should have distinct NS cable cost parameters for rural vs urban settlement types (e.g. 80–100 k€/km vs 125–200 k€/km).[2][3]

4. Role of smart measures (rONT, Spitzenkappung, 14a EnWG)

Your word document already touches on flexibility measures; the attached sources give quantitative support:

- rONT can reduce NS investment by >30 % in a subset of nets where voltage issues dominate, but is cost‑effective in only 5–11 % of NS grids; elsewhere conventional reinforcement is cheaper.[3][2]

- Flächendeckende Spitzenkappung of generation reduces MV+NS reinforcement by up to ~25 %, at the cost of compensation payments and control infrastructure.[2][3]

- 14a EnWG‑based curative load management can delay LV expansion by ~5–6 years on average in ambitious scenarios, but does not fully replace the need for reinforcement.[1]

In your cost model, these mechanisms can be represented as multipliers on required reinforcement volumes (and possibly additional control‑system cost terms), constrained by regulatory and customer‑acceptance limits.[1][3][2]

5. How to estimate trenching costs

As far as the available official and scientific sources go, there are no published percentage figures for how many LV grid routes in Germany already have spare ducts for parallel cables versus how often streets would need to be reopened.

What is (and isn’t) statistically tracked

- The Bundesnetzagentur “Zustand und Ausbau der Verteilernetze” reports collect data on cable lengths by voltage level, new build vs reinforcement, underground vs overhead, etc., but they do not include an indicator for “Leerrohre vorhanden / nicht vorhanden” in LV routes.[bundesnetzagentur]

- Systematic asset data on ducts (empty pipes alongside cables) exist only in DSO-internal GIS / asset registers and are not aggregated or published nationally.[ppl-ai-file-upload.s3.amazonaws]

So from national statistics you can derive, for example, that the majority of LV lines are underground cables, but not whether those trenches contain spare ducts for future parallel cables.[enbw]

What the planning literature says qualitatively

The attached studies and guidelines confirm that laying ducts with the first reinforcement is recommended practice, but they always describe this as a planning principle rather than a quantified existing share:

- Wintzek’s urban LV guideline explicitly recommends that when you open trenches in urban LV grids, you should lay empty pipes at the same time, precisely to avoid repeated street reopening when parallel cables are needed later.[ppl-ai-file-upload.s3.amazonaws]

- Fraunhofer’s 2025 study on future distribution grid planning notes that many DSOs already “verlegen zusätzliche Leerrohre oder halten Flächen für Erweiterungen frei”, but this is reported as an example of good, forward-looking practice, again without any nationwide percentage for how often it is actually done in existing LV grids.[ppl-ai-file-upload.s3.amazonaws]

- The Baden-Württemberg Verteilnetzstudie’s cost model distinguishes first-time cable installation (with full Tiefbau) from subsequent measures, but also does not contain data on how much of the existing LV network already has ducts available; it treats the “first reinforcement vs later parallel line” distinction as a modelling assumption.[ppl-ai-file-upload.s3.amazonaws]

In other words: all three strands of evidence say “you should install ducts when you open the street”; none of them say “X % of today’s LV routes already have ducts”.[ppl-ai-file-upload.s3.amazonaws]

Implications for your cost estimation

Given this data situation:

- You cannot reliably derive a national percentage for “no street reopening needed” from existing official or academic sources. Any specific percentage would be an assumption, not an empirically backed statistic.

- For a robust model, the usual approach is to treat “ducts available” as a scenario parameter and calibrate it with:

  - targeted queries to a few representative DSOs (urban vs rural, large vs small), and

  - your own sample of LV asset data where available.[ppl-ai-file-upload.s3.amazonaws]

For your heuristic you can therefore:

- Keep two cost levels (first reinforcement with Tiefbau vs later cable in duct),

- But be explicit that the share of routes in the second category is an assumption, not an observed national figure, and ideally document the DSO feedback behind whatever value you choose.

If you like, we can sketch a survey template or data request you could send to DSOs to get at least order-of-magnitude empirical input for different settlement types, which is likely the only way to make this critical parameter less speculative.

Example consolidated tables for your final overview

To support your request for clear tables, here is an example structure you can adopt or refine.

Table 3 – Recommended heuristic cost ranges for LV reinforcement (Germany)

| Measure | Category | Recommended range (Germany) | Key sources |
| --- | --- | --- | --- |
| NS cable reinforcement incl Tiefbau | Rural | 80–120 k€/km | BW‑study, PuBStadt[3][2] |
|  | Urban | 125–200 k€/km | BW‑study, PuBStadt[3][2] |
| NS cable parallel in empty pipe | Any | 20–60 k€/km | PuBStadt 17.2[2] |
| LV transformer replacement (same type) | Any | 10–15 k€ per unit | BW‑study 11; PuBStadt 17.2[3][2] |
| New LV secondary substation (ONS) | Any | 45–60 k€ per station | BW‑study 10[3] |
| rONT vs standard ONT premium | Any | +30–45 k€ per transformer | BW‑study 12[3] |
| MS cable reinforcement | Any | 130–160 k€/km | BW‑study 9[3] |
| New MS/LV transformer station | Any | 1.3–3.2 M€ per station | BW‑study 6,7[3] |

Table 4 – Macro‑level benchmark numbers

| Indicator | Value / range | Source |
| --- | --- | --- |
| National Verteilnetz expansion need 2022–2032 | 42.27 bn € total (all levels)[4][5] | BNetzA Bericht 2022[4][5] |
| Aggregated lower‑level (MS/NS) expansion 2022–2032 | 25.84 bn €[4][5] | BNetzA Bericht 2022[4][5] |
| NS share of BW distribution grid investment 2015–2030 | ~20–30 % of MS+NS total | Verteilnetzstudie BW[3] |
| LV expansion cost doubling between conservative vs ambitious electrification | Factor ≈2 in WEI202 DGLA 2045 | WEI202[1] |

You can extend these tables by adding columns for “your current assumption” and “difference vs benchmark” to explicitly show where your heuristics match or need adjustment.

How to integrate this into your model

Putting it all together, a validated heuristic cost estimation approach for your LV grid loading model would:

- Use official unit‑cost ranges above for NS cables, transformers, stations, and MS reinforcements, differentiated by settlement type.

- Model first vs subsequent reinforcement separately, assigning Tiefbau costs only to the first, and lower “empty‑pipe” costs to additional parallel cables.

- Include optional smart‑grid measures (rONT, Spitzenkappung, 14a control) as reduction factors on reinforcement volumes with their own cost terms.

- Check aggregated results against BNetzA and major Verteilnetzstudien to ensure your total expansion cost is in a realistic national corridor.

If you share the specific per‑meter and per‑transformer values currently used in your word document, we can walk through a line‑by‑line comparison against these benchmarks to highlight where they are already well‑supported and where further adjustment or differentiation (e.g., between first and subsequent reinforcements) would improve accuracy.

⁂

- WEI202-2.pdf

- Wintzek2021-Planungs-und-Betriebsgrundsatze-fur-stadtische-Verteilnetze-4.pdf

- Verteilnetzstudie_BW-3.pdf

- https://www.bundesnetzagentur.de/DE/Fachthemen/ElektrizitaetundGas/NEP/VerteilerNetz/start.html

- https://de.statista.com/statistik/daten/studie/1338912/umfrage/kosten-fuer-netzausbau-bis-2030/

- Bundesnetzagentur2025-AgNes-Diskussionspapier-8.pdf

- dena2025-Verteilnetzstudie_II-9.pdf

- Fraunhofer2025-Planung-von-Verteilnetzen-der-Zukunft-10.pdf

- German-LV-Grid-Expansion-Cost-Analysis-11.docx

- German-LV-Grid-Expansion-Cost-Analysis-12.docx

- https://www.bundesnetzagentur.de/DE/Fachthemen/ElektrizitaetundGas/VerteilerNetz/_DL/ZustandAusbauVerteilernetze2022.pdf?__blob=publicationFile&v=1

- https://www.dena.de/fileadmin/dena/Publikationen/PDFs/2025/dena_Verteilnetzstudie_II.pdf

- https://www.dena.de/fileadmin/dena/Publikationen/PDFs/2025/Gutachten_VNSII.pdf

- https://www.dena.de/fileadmin/dena/Publikationen/PDFs/2025/Verteilnetzstudie_II/dena-Verteilnetzstudie_II_Webinar_6_Finanzierung_der_Verteilnetztransformation.pdf

- https://www.dena.de/fileadmin/dena/Dokumente/Pdf/9100_dena-Verteilnetzstudie_Abschlussbericht.pdf

- https://www.cines.fraunhofer.de/content/dam/zv/cines/dokumente/publikationen/energiesystem/2025-Systemanalyse-Empfehlungen-Industrie.pdf

- https://www.dena.de/infocenter/dena-verteilnetzstudie-ii/

- https://data.bundesnetzagentur.de/Bundesnetzagentur/SharedDocs/Mediathek/Taetigkeitsberichte/2023/taetigkeitsberichttk20222023.pdf

- https://www.osti.gov/etdeweb/servlets/purl/21401027

- https://cdn.swk.de/assets/download/OLT_NGN_Partner_Talk_OLT10yr_2025_FINAL.pdf

- https://data.bundesnetzagentur.de/Bundesnetzagentur/SharedDocs/Mediathek/Monitoringberichte/monitoringberichtenergie2022.pdf

- https://www.netzentwicklungsplan.de/nep-file-download?file=dena-netzstudie_ii.pdf

- https://www.bundesnetzagentur.de/DE/Fachthemen/ElektrizitaetundGas/VerteilerNetz/Smard_Artikel.html

- NEP2035_Nachfrage-Bedarfsermittlung-2.pdf

- Abschlussbericht_dena-Netzstudie_III-5.pdf

- Bundesnetzagentur2022-Zustand-und-Ausbau-der-Verteilernetze-7.pdf

- Agora2024-Haushaltsnahe-Flexibilitaten-nutzen-6.pdf